## Sheet1
Type | Question Text | A | B | C | D | E | F | G | Correct Answer | Points
Single | What is the voltage that feeds QF1 of the BESS containers for auxiliary power? | 24 VDC | 480 VAC | 48 VDC | 690 VAC |  |  |  | B | 5
Single | What communication tool is used to connect to the Liquid Cooling Controller? | CAN Bus | ComTool/Ethernet | WiFi | Bluetooth |  |  |  | B | 5
Single | What is the default IP address for ETH2 on both the LC and BSC? | 192.168.12.100 | 192.168.0.100 | 192.168.13.100 | 192.168.0.50 |  |  |  | C | 5
Single | 0.5C (2 hour) variants of the battery containers have __ load switches in the Battery Collection Panel and __ PCS units per rack. | 6, 2 | 3, 2 | 6, 1 | 3, 1 |  |  |  | C | 5
Single | The Main AC Circuit Breakers (QF1 and QF2 of the SCC) automatically open upon pressing 'OFF' in the Local Controller Web Page. | TRUE | FALSE | [5 empty] | B | 5
Single | In order to safely de-energize/isolate the PowerTitan 2.0, which document should ultimately be referenced? | The site-specific Isolation Procedure | Central PV Customer LOTO Guidance | ST5015UX System Manual | Common sense |  |  |  | A | 5
Single | What is nominal AC output voltage (VAC) of the Battery Collection Panel? | 645 | 690 | 530 | 480 |  |  |  | B | 5
Single | When should the MSDs be initially installed? | They are installed out of factory | Hot Commissioning | Cold Commissioning | Post-Commissioning |  |  |  | B | 5
Single | Which of the these is responsible for the passive balancing of battery cells within each pack? | BMU | PCS | BSP | ARM Board |  |  |  | A | 5
Multi | To replace the PCS, which of the following operations are required? | Drain the PCS coolant | De-energize/Isolate the system block | Remove the sealing plates in front of the PCS transfer box | Remove Capacitor Bank | Inject Coolant |  |  | B, C | 5
Multi | Which of the following are components on the MVS5140 transformer (excluding anything in the SCC)? | Load Switch | Pressure gauge | AC circuit breaker | Off-load tap changer | Oil level indicator | Pressure relief valve | Door Switch | A,B,D,E,F | 7
Multi | Which of the following are functions of the LC300? | LC Firmware Upgrade | BSC Firmware Upgrade | Auto-denergization | Liquid Cooling Unit Parameter Configuration | SOC Protection Parameter modification |  |  | A,B,E | 5
Single | If the coolant pH falls below 7.3, it is required to replace the coolant | TRUE | FALSE | [5 empty] | A | 3
Single | You can upgrade the firmware of every BSC connected to an LC through the LC web portal. | TRUE | FALSE | [5 empty] | A | 3
Single | The power-on switch on the injection/drainage tooling must be turned on to drain the coolant | TRUE | FALSE | [5 empty] | B | 4
Single | In case of extreme weather conditions like sandstorms, thunderstorms, high winds, hail, battery container doors can still be opened. | TRUE | FALSE | [5 empty] | B | 4
Single | As long as I have properly isolated/de-energized the skid, I may replace a BMU board without insulating gloves. | TRUE | FALSE | [5 empty] | B | 4
Text | According to the General Isolation Procedure (not to be used on site), name in order the testing points for de-energization, and what voltage mode (AC or DC) they need to be tested for. Also list, what are the 3 measurement-related equipment (not PPE) needed to safely test for de-energization. | [8 empty] | 20